Fire Safety Plan

__________________________________________________________________________________________

(Building/Business Name)

__________________________________________________________________________________________

(Building Address)

Prepared By: ______________________________

Date: ____________________________________

Reviewed By: ______________________________

Signature: _________________________________

Annual Document Review

| Date | Name | Initials/Signature |
| --- | --- | --- |

Introduction	3

Submission Procedures	3

Building Resource Checklist	4

General Information	4

Contact Information	7

Building Owner(s)	7

Staff Members	7

Emergency Numbers	8

Non-Emergency Numbers	8

Contractor Contacts	8

Supervisory Staff Responsibility	10

Appointed Supervisory Staff	10

Persons Requiring Assistance	10

Building Owner(s) Responsibility	10

Emergency Procedures	12

If Fire or Smoke is Discovered	12

If You Are Trapped	12

Fire Extinguishment, Control or Confinement	13

Portable Fire Extinguisher Types	13

Fire Watch	14

Hot Works	14

Fire Drills	15

Safety to Life	16

Fire and Life Safety Equipment Maintenance	16

Equipment Maintenance Chart	17

Definitions	26

Appendix A	29

Appendix B	30

Introduction

Fire emergency procedures shall be provided for the follow:

- Every building containing an assembly, care, treatment or detention occupancy.

- Every building with a fire alarm system.

- Demolition and construction sites.

- Storage areas for combustible products and dangerous goods.

- Areas where flammable liquids or combustible liquids are stored or handled.

- Areas where hazardous processes or operations occur.

The implementation of the Fire Safety Plan helps to ensure effective utilization of life safety features in a building to protect people from fire. The required Fire Safety Plan should be designed to suit the resources of each individual building or complex of buildings. It is the responsibility of the owner to ensure that the information contained within the fire safety plan is accurate and complete.

Supervisory staff shall be trained in the fire emergency procedures described in the fire safety plan and proved a copy before they are given any responsibility for fire safety.

The fire safety plan shall be reviewed at intervals not greater than 12 months to ensure that it takes account of changes in the use and other characteristics of the building.

This official document is always to be kept readily available for use by the fire department, supervisory staff and other personnel.

The fire safety plan shall be located at the main entrance if the building or facility has dangerous goods, flammable liquid stored or handled, hazardous processing or operation, or if the building is classified as a high rise.

The fire safety plan location is: _________________________________________________

Submission Procedures

One copy of the fire safety plan must be submitted to the Fire Prevention Branch for review.

Fire Prevention Branch:

200 Saprae Creek Trail
Fort McMurray AB T9H 4P1
Phone: 780-792-5519
Fax: 780-743-3800
Email: RESFire.PreventionBranch@rmwb.ca

Building Resource Checklist

General Information

Occupancy Type:	 Assembly (A)     Care, Treatment, or Detention (B)     Residential (C)

 Business and Personal Services (D)    Mercantile (E)     Industrial (F)

Year of Construction:

Type of Construction:

  Combustible

  Non-Combustible

Fire Department Key Box:	  Yes 	  No

Muster Point Location: ________________________________________________________

Main Electrical Shut-Off Location: ________________________________________________

Main Gas Shut-Off Location: ____________________________________________________

Main Water Shut-Off Location: __________________________________________________

Fire Alarm System:			  Yes 	  No

  Single Stage System

  Two Stage System

Fire Alarm Annunciator Panel:		  Yes 	  No

Fire Alarm Panel Location: _____________________________________________________

Fire Alarm Make and Model: ___________________________________________________

Fire Signal Receiving System:		  Yes 	  No

Panel Location: _____________________________________________________

Make and Model: ___________________________________________________

Sprinkler System:			  Yes 	  No

  Wet-Pipe System

  Dry-Pipe System

Standpipe and Hose System:		  Yes 	  No

  Automatic System

  Wet		  Dry

  Manual System

  Wet		  Dry

  Hoses

Fire Pump:				  Yes 	  No

  Diesel

  Electric

*See attached size and operating instructions in appendices.

Private Fire Hydrant(s):			  Yes 	  No
Location(s): _________________________________________________________________

Portable Fire Extinguishers:		  Yes 	  No

Emergency Lighting Units:		  Yes 	  No

Emergency Generator:			  Yes 	  No
  Diesel
  Gas
* See attached description and operating instructions in the appendices.

Commercial Cooking Equipment:	  Yes 	  No

  Kitchen Exhaust System

  Fire-Extinguishing System

Make and Model: ___________________________________________________

Special Suppression System:		  Yes 	  No

Type: ___________________________________________________________________

Activation:

 Automatic

 Manual   	Location of activation: __________________________________

* See attached operating instructions for manual activation in the appendices.

Area of Coverage: _________________________________________________________

Elevator(s):				  Yes 	  No  
	 Automatic Recall
	 Fire Fighter Control
	*See attached fire department operating instructions in the appendices.

Smoke Alarms:				  Yes 	  No

Carbon Monoxide Detection:		  Yes 	  No

Location: _______________________________________________________________

Fire Dampers:				  Yes 	  No

Locations: _______________________________________________________________

Dangerous Goods:			  Yes 	  No

*If yes, attach document(s) identifying product classification, location of product, method of storage and size requirements, maximum quantity permitted in each storage area, sprinkler/fire alarm design criteria, control procedures for storage areas, spilled liquids procedures and fire department access routes.

Contact Information

Building Owner(s)

Name: _____________________________

Address: ___________________________

___________________________________

Phone: ____________________________

Staff Members

Name: _____________________________

Position: ___________________________

Phone: ____________________________

Name: _____________________________

Address: ___________________________

___________________________________

Phone: ____________________________

Name: _____________________________

Position: ___________________________

Phone: ____________________________

Name: _____________________________

Position: ___________________________

Phone: ____________________________

Name: _____________________________

Position: ___________________________

Phone: ____________________________

Name: _____________________________

Position: ___________________________

Phone: ____________________________

Name: _____________________________

Position: ___________________________

Phone: ____________________________

Name: _____________________________

Position: ___________________________

Phone: ____________________________

Name: _____________________________

Position: ___________________________

Phone: _____________________________

Emergency Numbers

| Contact | EMERGENCY Phone Number | NON-Emergency Phone Number |
| --- | --- | --- |
| FIRE/RESCUE/AMBULANCE | 911 | 780-743-7000 |
| POLICE (RCMP) | 911 | 780-788-4040 |
| Water Utility Company |  |  |
| Electricity Utility Company |  |  |
| Gas Utility Company |  |  |

Non-Emergency Numbers

| Contact | Phone Number |
| --- | --- |
| Regional Municipality of Wood Buffalo | 780-743-7000 |
| Fire Prevention Branch | 780-792-5519 |
| Building Manager |  |

Contractor Contacts

| System/Equipment | Company Name | Phone Number |
| --- | --- | --- |
| Fire Alarm System |  |  |
| Fire Monitoring System |  |  |
| Fire Sprinkler/Standpipe System |  |  |
| Fire Extinguishers |  |  |
| Emergency Lighting and Exit Signs |  |  |
| H.V.A.C. System |  |  |
| Emergency Generator |  |  |
| Fire Dampers |  |  |
| Kitchen Exhaust System |  |  |
| Kitchen Fire-Extinguishing System |  |  |

Supervisory Staff Responsibility

Supervisory staff must be assigned by the building owner and adequately trained in emergency procedures such as moving people to evacuate in an orderly manner and carrying out appropriate fire control measures. Supervisory staff must also have a good understanding of the fire protection systems located in the building and the required maintenance.

Appointed Supervisory Staff

Name: _____________________________

Position: ____________________________

Number: ____________________________

Name: _____________________________

Position: ____________________________

Number: ____________________________

Name: _____________________________

Position: ____________________________

Number: ____________________________

Name: _____________________________

Position: ____________________________

Number: ___________________________

Persons Requiring Assistance

Some occupants may require special assistance during evacuation. Preplanning is required to determine what may limit an occupant to evacuate. In residential occupancies staff should be aware of rooms occupied by persons requiring special assistance and should inform the responding fire department.

| Location | Name | Reason |
| --- | --- | --- |

Additional Information: _________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

Building Owner(s) Responsibility

The owner or the owner’s authorized agent is responsible for carrying out the provisions of the Code and for developing the fire safety plan.

Responsibilities include but are not limited to:

- Establish emergency procedures to be followed at the time of an emergency.

- Appointment and organization of designated supervisory staff to carry out safety duties.

- Training of supervisory staff and other occupants so that they are aware of their responsibilities for fire safety.

- Holding of fire drills required by the Nation Fire Code Alberta Edition.

- Control of fire hazards in the building.

- Maintenance of building facilities and areas for access during an emergency.

- Provisions of alternate measures for safety of occupants during shut down of fire protection equipment.

- Ensuring that all tests, inspections and maintenance records for any fire or life safety equipment mentioned in this document are retained on the premises so that the current and provided to a Fire Safety Codes Officer upon request.

- Ensuring that initial verification or test reports for fire protection systems are retained throughout the life of the systems.

- Post and maintain at least one copy of the fire emergency procedures on each floor area.

- Create a floor diagram and indicate designed use of the rooms.

- Keep a copy of the fire safety plan on the premises in an approved location.

- Ensure that the information in the fire safety plan is current and reviewed and updated if necessary, every 12 months.

- Designate and train alternate staff to replace supervisory staff during any absence.

- Notify the fire department if a spill or leak of 50 L or greater has occurred involving flammable or combustible liquids.

Emergency Procedures

If Fire or Smoke is Discovered

All supervisory staff shall do the following:

- Stay calm.

- Leave the affected area and close all doors behind you. Do not lock the doors.

- Initiate the fire alarm system by activating the pull station in the corridor.

  - Ensure 911 is notified.

- Alert nearby occupants of the emergency and of the muster point.

- If the fire is in the early stages, use the building’s firefighting equipment if safe to do so.

- Leave the floor area via the stairways, do not use an elevator.

  - If you encounter fire or smoke use an alternative exit.

- Call the fire department at 911 when safe to do so.

- Meet the fire department outside the main entrance, muster point or wherever directed by dispatch. Provide access and assistance to fire crews if directed.

- Do not re-enter the building until it is declared safe by the fire department.

- Do not shut off the any fire protection systems unless directed by the fire department.

Every fire situation can be different so emergency procedures need to be addressed for every type of emergency. A well understood and practiced emergency response plan based on specific building hazards can help minimize stress during an emergency.

If You Are Trapped

- Find a safe area, close the door and keep it unlocked.

- Seal off all openings such as around a door with clothes or towels. Wetting them can help.

- Stay low if there is smoke.

- Get to a window and open it if there is fresh air and yell to anyone regarding your location.

- Call 911 and let them your location in the building.

Fire Extinguishment, Control or Confinement

Portable Fire Extinguisher Use

In the event a small fire cannot be extinguished with the use of a portable fire extinguisher or the smoke presents a hazard for the operator, the door to the area should be closed to confine and contain the fire.  Leave the fire area.  Ensure that the fire alarm system has been activated and that fire department has been notified prior to an attempt to extinguish the fire.  Only those persons who are trained and familiar with extinguisher operation may attempt to fight the fire.

Use the acronym P.A.S.S. to remember the fire extinguishing sequence:

P - Pull the pin in the handle.

A - Aim the nozzle at the base of the fire.

S - Squeeze the leaver slowly.

S - Sweep from side to side until the fire is out or until the cylinder is empty.

Portable Fire Extinguisher Types

|  | Class A | For use on fires involving wood, cloth, paper, rubber, and many plastics. |
| --- | --- | --- |
|  | Class B | For use on fire involving flammable liquids, combustible liquids, petroleum greases, tars, oils, oil-based paints, solvents, lacquers, alcohols, and flammable gases. |
|  | Class C | For use on fires that involve energized electrical equipment. |
|  | Class D | For use on fires involving combustible metals, such as magnesium, titanium, zirconium, sodium, lithium, and potassium. |
|  | Class K | For use on fires involving cooking appliances that use vegetable or animal oils and fats. |

Fire Watch

When is Fire Watch Required?

A “Fire Watch” is a dedicated person or persons whose sole responsibility is to look for fires within an established area. Fire watch is required during the following events:

- When any part of a fire alarm system is impaired or inoperable.

- When any part of a sprinkler or standpipe system is impaired or inoperable.

- When any part of a special suppression system is impaired or inoperable.

- When hot works is being done.

Responsibilities and duties include:

- Be familiar with the building and procedures for sounding an alarm in the event of a fire.

- Watch out for fire hazards in the workplace while work is performed by other employees.

- Maintain the conditions and requirements stated on the Hot Works permit.

- Keep flammable materials from ignition sources.

- In the event of fire, extinguish it immediately or activate the fire alarm.

- Call 911.

- Stop operations if you find any hazardous condition.

- Never leave the job site while the work is being done unless another Fire Watch can replace you.

- When all operations are done, do not leave the worksite unless you’re sure that there are no hot sparks, hot embers and other fire hazards unless another fire watch or fire monitor is assigned.

A sufficient number of Fire Watch shall be assigned to make at least one complete patrol of the affected area every 15 minutes. Fire Watch patrols shall be recorded and made available upon request by a Fire Safety Codes Officer. More information can be found on the RMWB website: www.rmwb.ca

Hot Works

Hot works conducted in a building that is outside of a designated work area, requires a permit from the Fire Prevention Branch. If hot works are being conducted in a building with a fire alarm or sprinkler system, measures must be in place to prevent nuisance alarms. Notification to the fire department dispatch (780-743-7061) must be made before hot works start and prior to fire safety equipment being shut down. Fire watch procedures are to be implemented in the affected areas during and after hot works. More information can be found on the RMWB website: www.rmwb.ca

Fire Drills

The person in charge of the building is responsible for determining the procedures of the fire drill and must document each drill. Records of the drills must include the date of the drill, evacuation time and any comments and recommendations. Drill records are to be kept onsite for 2 years and provided to a Fire Safety Codes Officer upon request.

The procedures for conducting the fire drill should take into consideration the following:

- The building occupancy and its fire hazards.

- The safety features and equipment provided in the building.

- The desirable degree of participation of occupants other than supervisory staff.

- The number and degree of participating supervisory staff.

- The requirements of the fire department.

Frequency

Fire drills are to be held at the following frequencies (check appropriate box):

 Every 2 months for high rise buildings.

 Every 3 months for a laboratory.

 3 times in each of the fall and spring term for school attended by children.

 Every month for day-care centers, treatment or detention occupancy.

 Every 12 months for all other occupancies.

A fire drill template can be found on the RMWB: www.rmwb.ca

Safety to Life

The appointed person(s) must ensure the following:

- Fire separations are not damaged.

- Doors in fire separations are not damaged and kept closed.

- Accumulation of combustible waste material in and around buildings is removed.

- Combustible material is not stored in means of egress, service rooms or service spaces.

- Aisles and exits are kept clear, unobstructed and in good repair.

- Snow or ice in exterior passageways and stairs is removed.

- At least one copy of the fire emergency procedures is posted on each floor area.

- Laundry lint traps, vents and piping to prevent lint accumulation is kept clean.

- Ashtrays are provided for designated smoking areas.

- Fire department access to building is clear and unobstructed.

- <Add additional site-specific instructions, if applicable >

Fire and Life Safety Equipment Maintenance

Maintenance on fire and life safety equipment is done at different frequencies. The maintenance is completed the following ways:

- Test means the operation of a device or system to ensure that it will perform in accordance with its intended operation or function.

- Inspect means visual examination to determine that the device or system will perform in accordance with its intended function.

- Maintenance means the process of preserving a condition or situation.

Equipment Maintenance Responsibility Chart

Below is a list of different fire and life safety equipment, their maintenance requirements and who is responsible for carrying out these tasks. (Note: this is a general list, more maintenance may be required depending on the type of equipment located at the building.)

General Safety Equipment Requirements

| General Safety Equipment National Fire Code - Alberta Edition | Responsibility |
| --- | --- |
| Records of tests, inspections, maintenance or operational procedures shall be retained so that at least the current and the immediately preceding records are available. |  |
| Weekly |  |
| When heating, ventilating and air-conditioning appliances subject to accumulation of combustible deposits, hoods, filters and ducts shall be inspected and cleaned when deposits create a fire hazard. |  |
| Yearly |  |
| Fire dampers, smoke dampers, combo smoke/fire dampers and fire-stop flaps shall be inspected. |  |
| Every chimney, flue and flue pipe shall be inspected and cleaned as often as necessary to keep them free from accumulations of combustible deposits. (Increase frequency if needed) |  |
| Disconnect switches for mechanical air-conditioning and ventilating systems shall be inspected to establish that the system can be shut down in an emergency. |  |
| 4 Years |  |
| Fire dampers, smoke dampers, combination smoke/fire dampers and fire-stop flaps shall be tested. |  |
| 6 Years |  |
| Fire dampers, smoke dampers, combination smoke/fire dampers and fire-stop flaps shall be tested (Hospitals only) |  |

Doors and Means of Egress Requirements

| Doors and Means of Egress National Fire Code - Alberta Edition | Responsibility |
| --- | --- |
| Exit door hardware shall be in good working condition and the door shall not be bolted, barred or locked. |  |
| Doors in fire separations shall not be obstructed, blocked or wedge open. |  |
| Daily |  |
| Doors in fire separations shall be inspected to ensure they remain closed. |  |
| Monthly |  |
| Doors in means of egress shall be tested to ensure they are operable. |  |
| Yearly |  |
| Safety features of a revolving door shall be tested. |  |
| Sliding doors that swing vertically for egress shall be tested. |  |
| Doors with electromagnetic locks shall be tested. |  |

Smoke Alarms Requirements

| Smoke Alarms CAN/ULC-S552 – Inspection, Testing and Maintenance of Smoke Alarms & National Fire Code - Alberta Edition | Responsibility |
| --- | --- |
| Weekly |  |
| Inspect the status of the power “on” indicator. |  |
| Monthly |  |
| Smoke alarms shall be inspected and tested. |  |
| Yearly |  |
| Smoke alarms shall be inspected, tested and cleaned in accordance with CAN/ULC-S552. |  |

Portable Fire Extinguisher Requirements

| Portable Fire Extinguishers NFPA 10 – Standard for Portable Fire Extinguishers | Responsibility |
| --- | --- |
| Each portable extinguisher shall have a tag securely attached to it showing the month and year maintenance was performed, person performing the work and the name of the agency performing the work. |  |
| All extinguishers shall be recharged after use or as indicated by an inspection or when performing maintenance. When recharging is performed, the recommendations of the manufacturer shall be followed. |  |
| Monthly |  |
| Fire extinguishers shall be inspected. |  |
| Annually |  |
| Extinguishers shall be subject to maintenance by a qualified person*. |  |
| 5 Years |  |
| Extinguishers with stainless steel shells require hydrostatic testing by a qualified person*. |  |
| 6 Years |  |
| Extinguishers with steel shells require to be emptied and Inspected by a qualified person*. |  |
| 12 Years |  |
| Extinguishers with steel shells require hydrostatic testing by a qualified person*. |  |

Fire Protection Signal Receiving Requirements

| Fire Signal Receiving Centres CAN/ULC-S561 – Standard for Installing and Services for Fire Signal Receiving Centres and Systems | Responsibility |
| --- | --- |
| 6 Months |  |
| All sprinkler control valves, and pressure switches shall be tested by a qualified person*. |  |
| Annually |  |
| Fire signal receiving systems shall be tested and inspected by a qualified person. |  |

Fire Alarm System Requirements

| Fire Alarm System CAN/ULC-S536 – Standard for Inspection and Testing of Fire Alarm Systems | Responsibility |
| --- | --- |
| Fire alarm and voice communication system components shall be kept unobstructed. |  |
| Fire alarm system power supply disconnect switches shall be locked in an approved manner. |  |
| Daily |  |
| Inspect status of primary power and trouble signals at the fire alarm panel to confirm operability. |  |
| Annually |  |
| Fire alarm systems shall be tested and inspected by a qualified person*. |  |

Emergency Lighting Requirements

| Emergency Lighting Units National Fire Code - Alberta Edition | Responsibility |
| --- | --- |
| Emergency lighting shall be maintained in operating condition. |  |
| Monthly |  |
| Emergency lighting units shall be tested and inspected in accordance with the National Fire Code Alberta Edition. |  |
| Exit signs with battery back-up shall be tested and inspected in accordance with the National Fire Code Alberta Edition. |  |
| Annually |  |
| Emergency lighting units shall be tested for a duration equal to the design criteria. |  |
| Charging conditions for voltage, current and recovery period shall be tested in accordance with the manufacturer’s specification. |  |
| Exit signs shall be inspected in accordance with the National Fire Code Alberta Edition. |  |

Sprinkler Systems – General Requirements

| Sprinkler Systems – General NFPA 25 – Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | Responsibility |
| --- | --- |
| Annually |  |
| Private fire hydrant(s) shall be tested and inspected by a qualified person*. |  |
| 5 Years |  |
| Sprinklers that are subjected to harsh environments shall be replaced, or representative samples shall be tested. |  |
| Solder-type sprinklers having extra high temperature classification that are exposed to maximum allowable ambient temperature conditions shall be tested. |  |
| 10 Years |  |
| Dry sprinklers shall be replaced, or representative samples shall be tested. (tests repeat every 10 years) |  |
| 20 Years |  |
| Sprinklers with fast-response elements shall be replaced, or representative samples shall be tested. (tests repeat every 10 years thereafter) |  |
| 50 years |  |
| Sprinklers shall be replaced or have representative samples tested. (tests repeat every 10 years) |  |

Standpipe and Wet Pipe Sprinkler Systems Requirements

| Standpipe & Wet Pipe Systems NFPA 25 – Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | Responsibility |
| --- | --- |
| Monthly |  |
| Gauges on wet pipe sprinkler systems shall be inspected to ensure that they are in good condition and have normal water supply pressure. |  |
| Quarterly |  |
| Waterflow and supervisory alarm devices shall be inspected to verify that they are free of physical damage. |  |
| Annually |  |
| Standpipe and hose systems shall be Inspected by a qualified person*. |  |

Standpipe & Wet Pipe Systems Continued

| Standpipe & Wet Pipe Systems NFPA 25 – Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | Responsibility |
| --- | --- |
| 5 Years |  |
| A flow test shall be conducted on an automatic standpipe and hose system by a qualified person*. |  |
| Gauges shall be replaced or tested by a qualified person*. |  |
| Check valves shall be inspected internally by a qualified person*. |  |

Dry Pipe Sprinkler System Requirements

| Dry Pipe Sprinkler Systems NFPA 25 – Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | Responsibility |
| --- | --- |
| Compressors used with dry pipe sprinkler systems shall be maintained in accordance with the manufacturer’s instructions. |  |
| Daily |  |
| Valve enclosure heating equipment shall be inspected during cold weather for its ability to maintain a minimum temperature of at least 4°C. |  |
| Monthly |  |
| Gauges shall be inspected to verify that the gauge is operable and not damaged. |  |
| Annually |  |
| Each dry pipe valve shall be trip tested during warm weather by a qualified person*. |  |
| 3 Years |  |
| Dry pipe valve shall be trip tested, with the control valve fully open, by a qualified person*. |  |
| 5 Years |  |
| Strainers, filters, and restricted orifices shall be inspected by a qualified person*. (More frequently if tests indicate as such) |  |

Backflow Prevention Assembly Requirements

| Backflow Prevention Assemblies NFPA 25 – Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | Responsibility |
| --- | --- |
| Weekly |  |
| Backflow reducing pressure assemblies and detector assemblies shall be inspected to ensure there is no continuous discharge from the relief port and that the OS&Y valves are in the open position. |  |
| Monthly |  |
| Valves that are electrically supervised or locked shall be inspected. |  |
| Annually |  |
| Backflow preventers installed in fire protection system piping shall be tested by a qualified person*. |  |
| 5 Years |  |
| Backflow prevention assemblies shall be inspected internally by a qualified person*. |  |

Fire Pump Requirements

| Fire Pumps NFPA 25 – Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | Responsibility |
| --- | --- |
| Weekly |  |
| Diesel engine–driven fire pumps shall be operated a minimum of 30 minutes with a qualified person* in attendance. |  |
| Pump house and pump systems shall be inspected by a qualified person*. |  |
| Monthly |  |
| Electric motor–driven fire pumps shall be operated a minimum of 10 minutes with a qualified person in attendance*. |  |
| Annually |  |
| Each pump assembly shall be flow tested by a qualified person*. |  |
| Each pump and accessories shall be maintained in accordance with the manufacture recommendations by a qualified person*. |  |

Restaurant Exhaust and Fire Suppression System Requirements

| Restaurant/Commercial Kitchen Exhaust and Fire Suppression Systems NFPA 96 – Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations | Responsibility |
| --- | --- |
| Hoods, grease removal devices, fans, ducts and other accessories shall be cleaned at frequent intervals to prevent the accumulation of grease or oily sludge. |  |
| The entire exhaust system shall be inspected for grease buildup by a qualified person* in accordance with the below table: - Solid fuel cooking operations – Monthly - High-volume cooking operations – Quarterly - Moderate-volume cooking operations – Semiannually - Low-volume cooking – Annually |  |
| Where the fire-extinguishing system or exhaust system is nonoperational or impaired, the systems shall be tagged as noncompliant, and the owner or owner’s representative shall be notified in writing of the impairment. |  |
| If the exhaust system is found to be contaminated with deposits from grease-laden vapors, the exhaust system shall be cleaned by a qualified person*. |  |
| Semiannually |  |
| Fire extinguishing systems (special fire suppression) shall be tested and maintained by a qualified person*. |  |
| Yearly |  |
| Inspection and cleaning (if necessary) behind cooking equipment, below surfaces, or in flue gas exhaust by a qualified person*. |  |

Wet Chemical Extinguishing System Requirements

| Wet Chemical Extinguishing Systems NFPA 17A – Standard for Wet Chemical Extinguishing Systems | Responsibility |
| --- | --- |
| Monthly |  |
| Fire extinguishing equipment shall be inspected in accordance with manufacture specifications. |  |
| Semiannually |  |
| Fire extinguishing systems shall be tested and maintained by a qualified person*. |  |
| 12 Years |  |
| Fire extinguishing equipment shall be hydrostatically tested. |  |

Clean Agent Extinguishing System Requirements

| Clean Agent Fire Extinguishing Systems NFPA 2001 – Standard for Clean Agent Fire Extinguishing Systems | Responsibility |
| --- | --- |
| Semiannually |  |
| The agent quantity and pressure shall be inspected. |  |
| Annually |  |
| Fire extinguishing system shall be inspected and tested by a qualified person*. |  |
| 5 Years |  |
| Hoses shall be tested. |  |

Emergency Power System Requirements

| Emergency Power Systems CSA C282 – Emergency Electrical Power Supply for Buildings | Responsibility |
| --- | --- |
| A quantity of fuel sufficient for operating the engine under maximum load for at least 2 hours shall be maintained on site. (24 hours for care or detention occupancies) |  |
| Manuals containing mechanical and electrical drawing, and instructions for operation and maintenance shall be kept available for use by staff. |  |
| Weekly |  |
| Emergency power systems for health care facilities shall be tested. |  |
| Monthly |  |
| Emergency power systems shall be tested. |  |
| Annually |  |
| Emergency power systems shall have a 2-hour full-load test. |  |

* a qualified person is someone who has acquired training, or an approved certificate of training as required by the National Fire Code, Alberta Edition.

Definitions

Assembly Occupancy means the occupancy or the use of a building, or part thereof, by a gathering of persons for civic, political, travel, religious, social, educational, recreational or like purposes, or for the consumption of food or drink.

Backflow Prevention Assembly is a device used to protect potable water from being contaminated do to water backflow.

Business and Personal Services Occupancy means the occupancy or use of a building or part thereof for the transaction of business or the rendering or receiving of professional or personal services.

Care Occupancy means the occupancy or use of a building or part thereof where care is provided to residents.

Clean Agent Extinguishing System uses inert gases and chemical agents that are electrically non-conducting and leave no residue upon evaporation to extinguish a fire. These are generally used to protect high value equipment such as telecommunication equipment.

Detention Occupancy means the occupancy by persons who are restrained from or are incapable of evacuating to a safe location without the assistance of another person because of security measures not under their control.

Dry Pipe Sprinkler System – are installed in areas that have the potential to freeze. There is no water in the sprinkler pipe, instead the pipes are filled with pressurized air or nitrogen.

Exit means that part of a means of egress, including doorways, that leads from the floor area it serves to a separate building, an open public thoroughfare, or an exterior open space protected from fire exposure from the building and having access to an open public thoroughfare.

Fire Alarm System has different devices working together to detect a fire and notify people throughout a building. Some devices that are part of a fire alarm system are manual pull stations, smoke detectors, heat detectors, bell, horns and strobes.

Fire Damper means a closure consisting of a damper that is installed in an air distribution system or a wall or floor assembly and that is normally held open but designed to close automatically in the event of a fire in order to maintain the integrity of the fire separation.

Fire Extinguisher is a fire protection device used to extinguisher or control a small fire.

Fire Separation means a construction assembly that acts as a barrier against the spread of fire.

Fire Watch means to keep watch for outbreaks of fire, as a duty or responsibility.

High-Volume Cooking includes 24-hour cooking, charbroiling, or wok cooking.

Hot Works means the burning, welding, heating of a material, or a similar operation that is capable of initiating fires or explosions including, but not limited to, cutting, welding, Thermit welding, brazing, soldering, grinding, thermal spraying, thawing pipe, torch-applied roofing or membrane, adhesive bonding, or any other similar heat-producing activity.

Industrial Occupancy (Group F) means the occupancy or use of a building or part thereof for the assembling, fabricating, manufacturing, processing, repairing or storing of goods and materials.

Inspect means visual examination to determine that the device or system will apparently perform in accordance with its intended function.

Kitchen Exhaust is the hood vent located over the cooking equipment. The exhaust fan inside the hood creates a reverse draw of air to remove grease vapours, smoke, steam and heat away from the building.

Kitchen Fire Suppression System is a fire extinguishing system that is designed specifically for grease fires. Discharge nozzles are installed in the hood and exhaust.

Low-Volume Cooking – includes churches, day camps, seasonal business or senior centres.

Means of Egress means a continuous path of travel provided for the escape of persons from any point in a building or contained open space to a separate building, an open public thoroughfare, or an exterior open space protected from fire exposure from the building and having access to an open public thoroughfare. Means of egress includes exits and access to exits.

Mercantile Occupancy means the occupancy or use of a building or part thereof for the displaying or selling of retail goods, wares or merchandise.

Moderate-Volume Cooking includes anything other than what is described as high or low volume cooking.

Owner means a lessee, a person in charge, a person who has care and control and a person who holds out that the person has the powers and authority of ownership or who for the time being exercises the powers and authority of ownership.

Residential Occupancy means the occupancy or use of a building or part thereof by persons for whom sleeping accommodation is provided but who are not harboured for the purpose of receiving care or treatment and are not involuntarily detained.

Smoke Alarm means a combined smoke detector and audible alarm device designed to sound an alarm within the room or suite in which it is located upon the detection of smoke within that room or suite.

Solid Fuel Cooking includes wood, charcoal, or coal for the cooking process.

Special Fire Suppression is a system designed to detect and extinguish fires in locations that are not suitable for standard fire suppression. Some areas that may have special fire suppression are server rooms, telecom rooms, or electrical rooms. These systems may be designed with dry/wet chemicals, clean agent, gas, or foam for the fire suppression agent.

Sprinkler System is a fire protection system designed to control and suppress a fire. These systems are comprised of water supply, network of piping and actuating devices.

Supervisory Staff means those occupants of a building who have some delegated responsibility for the fire safety of other occupants under the fire safety plan.

Test means the operation of a device or system to ensure that it will perform in accordance with its intended operation or function.

Treatment occupancy means the occupancy or use of a building or part thereof for the provision of treatment, and where overnight accommodation is available to facilitate the treatment.

Wet Chemical Extinguishing System utilized water and chemical based solution to extinguish a fire. These are generally found in areas were fires can involve materials burning at a high temperature such as commercial kitchens.

Appendix A

(Building Drawings)

Appendix B

(Operating Procedures, Dangerous Goods, Unique Risk Factors, etc.)